Go To Assist  Application Note

Number:	1

Date:		November 26th, 2012

Subject: 	Go To Assist Preference Settings

________________________________________________________________________

Control IQ can interface to SynergyMMS in the follow ways

- Run hours for equipment to trigger a Preventive Maintenance Schedule

- Generate a work request based on an alarm

- Control Green Guest Room Alarms

- Provide Meeting Room occupancy status

The basic connection between Control IQ and SynergyMMS, from the Control IQ side, is defined in the Control IQ  ‘Preferences’ Table

Key				Value	(example)

SynergyWSURL		demo.synergymms.com

SynergyPropertyID		34

Run Hours

SynergyMMS keeps a connection string to connect directly to the Control IQ database.

SynergyMMS defines a Control IQ ‘Alias’ to a SynergyMMS piece of equipment

When the SynergyMMS PM Generator is executed, it collects the run hours from Control IQ to evaluate against a threshold to trigger the PM Work Request.

Work Requests

A work request is setup as an Alarm Process in Control IQ

In the Output Type choose “SynergyMMS”

In the Output Detail enter the SynergyMMS TaskCode that will be generated

Control IQ will connect to SynergyMMS with a User of “ControlIQ”. This user must be defined in the SynergyMMS system.

The Control IQ Alias, and “alarm message” will be sent to Synergy to be appended to the work request.

Control Green

This is very similar to a work request.  Based on Alarms read from the Control Green Server (driver), Control IQ will send a work request to SynergyMMS.  Control IQ will connect to SynergyMMS with a User of “ControlIQ”. This user must be defined in the SynergyMMS system.  Control IQ will provide the following details as provide by the Control Green Server

Location=[from Control Green]

TaskCode=(either from the Personality Field or passed from CG Server)

Comments=[from Control Green]

EquipID=1078

Meeting Room Occupancy Status

Control IQ updates the SynergyMMS room status.  Effectively this adds the meeting spaces to the Guest Tab of SynergyMMS and shows the start/stop of the events.

If there is a valid event type and the current time is between the event start and end times, it will flag the room as sold/occupied, the event type (Luncheon, Break, Meeting) and provide the # of guests in the NumAdults field.  Otherwise it treats it like a checked out room.

In addition to the preferences table setting listed above, in the Control IQ database subsystems table

For the Delphi subsystem, in the personality field add

SynergyMMS=True

There is a cross reference table on the CIQ Delphi database called FunctionsSynergyMMSxrefs.  In this table is stored the cross reference between Delphi and SynergyMMS rooms.  Some examples:

RoomName				SynergyRoom

Sutton A				Sutton A

Sutton A and B			Sutton A

Sutton A and B			Sutton B

Sutton B				Sutton B

Sutton Suite				Sutton A

Sutton Suite				Sutton B

The SynergyRoom is the column that is passed to SynergyMMS