Documentation for Control IQ

Relating to:			CIQProc.EXE

Date:				June 13th, 2024

Program Revision:		5.0

Subject			Class Properties and Constants

CIQProc uses a system of object oriented variables throughout the program.  This is referred to as a class.object.property (COP).

Class – Defines the type of object that is being referenced.  Supported classes are:

AI			Points – Analog Inputs

AO			Points – Analog Outputs

ASIC1			Points – ASIC1 Controllers

DI			Points – Digital Inputs

DO			Points – Digital Outputs

LOGIC		Points – Logic (conversion)

LOOKUP		Points – Lookup

METER		Points – Meters

PID			Points – PIDs

PNT			Points – Generic for all points

REPORT		Points – Memorized Reports

TIMER		Points – Timers

SCHED		Points – Schedules

SYS			System Variables

SUB			Subsystem Variables

Object – This is the ‘alias’ portion of the COP.  It is the alias of the point, or schedule.  If the class being used is ‘SYS’ the object is predefined as ‘System’

Property – Is from this list of available properties listed below.

PNT may be used generically for the class of any ‘point’ with regards to common properties for all points.  Hence:

AI.OATemp.Value   is equivalent  to  Pnt.OATemp.Value

However, if you want to retrieve something specific to a point type, then the actual class must be use.  For example:

AI.OATemp.HighAlarm   is NOT retrievable as Pnt.OATemp.HighAlarm

Constants

All of these = 0

DayEven

Disable

Disabled

Gray

Grey

Off

Open

Opened

Even

False

Heat

MonthEven

UnOcc

UnOccupied

YearEven

All of these = 1

Close

Closed

Cool

DayOdd

Enable

Enabled

Green

MonthOdd

Occ

Occupied

Odd

On

PMS

True

YearOdd

All of these = 2

Night

NSB

NightSetBack

Yellow

All of these = 3

Red

All of these are additional key words (can’t be used as alias names)

Date

Day

Int

Max

Min

Month

Now

Time

Year

Display Format

Display Format is used in many Classes.  Its is decoded as

# - Place Holder

0 – Force a zero if not present

$ - Put the currency sign in the format

######.#	72  		is displayed as 	72.

72.1 		is displayed as 	72.1

72.12 		is displayed as 	72.1

72.17 		is displayed as 	72.2

.01		is displayed as 	.0

######.0	72  		is displayed as 	72.0

72.1 		is displayed as 	72.1

72.12 		is displayed as 	72.1

72.17 		is displayed as 	72.2

.01 		is displayed as	.0

#####.#0	.01		is displayed as	.01

.1		is displayed as 	.10

####0.#0	.01		is displayed as	0.01

.1		is displayed as	0.10

###,###.0	1234.56	is displayed as	1,234.6

$###,###.#0	1234.5	is displayed as	$1,234.50

Available Properties

Class - SYS

| AlarmsLast24Hours AlarmsLast7Days AlarmsLast30Days Alarmstate | - Number of alarms in the past 24 hours - Number of alarms in the past 7 days - Number of alarms in the past 30 days - 0= no alarms, 1 = one or more alarms, 3 = all ack |  |
| --- | --- | --- |
| AllowDynamics | - 1/0 if SLA is enforce |  |
| CIQGUI_Version | - The currently running GUI version |  |
| CIQProc_Version CommError CommStatus | - The currently running CIQProc Version - Normal or Trouble (Set to trouble if ANY point nocom) - Percentage of points with Comm Error |  |
| CPU | - The % of CPU Load (see RAMPCT) |  |
| Database | - The database DSN being used |  |
| DatabaseName | - The database name being used |  |
| Date DateTime | - present date MM-DD-YY - present date time MM-DD-YY HH:MM:SS |  |
| Dawn | - HHMM Sunrise + DuskDawn Offset |  |
| DayDateTime | - present format as ‘Friday 02-15-13 14:35’ |  |
| DayOdd | - a 1 if DOW = 1,3,5,7 else 0 |  |
| DayOfMonth | - present Day of Month (1-31) |  |
| DaysSinceLastBackup DOM, DAY | - Number of days since last backup default=999 - present Day of Month (1-31) |  |
| DOW | - present Day of Week (1-Sunday, 7=Saturday) |  |
| DOY,DayOfYear | - present Day of Year (1-365) |  |
| Dusk | - HHMM Sunset – DuskDawn Offset |  |
| DuskandDawn | - number of minutes before sunrise / after sunset |  |
| EnableWatchDog |  |  |
| ExceptionsOverrideStandard | - 1/0 set in Preferences |  |
| ForeCastTitle(x) | - Forecast title on the next x day |  |
| ForeCastImage(x) | - Forecast icon on the next x day |  |
| ForeCastDesc(x) | - Forecast text on the next x day |  |
| HoursSinceSAIntBeacon HoursSincePMSBeacon HoursSinceVoiceBeacon HHSeconds | - Hours since CIQ-SA Interface checked in - Hours since a PMS record was received - Hours since CIQ Voice checked in - present ((Minutes * 60) modulo 1800) |  |
| Holiday | - a 1 if this day is a holiday else 0 |  |
| Hours | - present hour (0-23) |  |
| LastBackUpDate | - Last Backup Date (since proc has been running) |  |
| Latitude | - The latitude of the site (dusk / dawn) |  |
| LimitedOperationLevel | - Bit mapped |  |
| LongDate | - present date January 23, 2004 |  |
| Longitude | - The Longitude of the site (dusk / dawn) |  |
| Memory | - Amount of memory being used by CIQProc |  |
| MinimumLogTime | - What is the minimum time to log to History (minutes) |  |
| Minutes | - present minute (0-59) |  |
| Month | - present Month (1-12) |  |
| MonthOdd | - a 1 if Month = 1,3,5,7,9,11 else 0 |  |
| MyIPAddress | - The IP Address of the CIQProc engine |  |
| Now | - present date time MM-DD-YY HH:MM:SS |  |
| PointsInAlarm PointsInAlarmPCT | - Number of Points In Alarm or Acknowledged - Percentage of Points that are in Alarm or Ack |  |
| ProcHealth | - returns “Normal” if proc is running ok |  |
| ProcIP | - What IP address is it listening on |  |
| PublicIPAddress | -Public facing IP (Mayne be the router) |  |
| QOD | - Quote of the day |  |
| RAMPCT | - Percentage of Available RAM used (See CPU) |  |
| ReInitMinutes | - How often to rescan lost address (in minutes) |  |
| ScanRate | - returns CISProc’s scan time (in seconds) |  |
| Season | - textual – Season name |  |
| Seconds | - present seconds (0-59) |  |
| ShortDate | - present date MM-DD-YY |  |
| ShortTime | - present time HH:MM |  |
| SiteName | - returns the site name from the preferences table |  |
| Status | - 0,1,2 as define in StatusText |  |
| StatusText | - Textual – ImOK or ImNOTok or ImPaused |  |
| Sunrise | - HH:MM of sunrise for the current day |  |
| Sunset | - HH:MM of sestet for the current day |  |
| Threadxxx.ScanTime | - Then duration of each thread |  |
| Time | - present time HH:MM:SS |  |
| txtDOW | - DOW as “Sunday, Monday, Tuesday…” |  |
| txtMonth | - Month as “January, February, March…” |  |
| UpSince | - returns date and time when proc was started |  |
| UpTime | - returns number of minutes Proc has been up |  |
| UserXX or User(xx) | -User assigned variables in Preferences |  |
| Version | - returns the version of CIQproc ‘v2.0.1.3’ |  |
| WeekOdd | - a 1 if week of the year is 1,3,5,7, etc else 0 |  |
| WindowState | -normal/minimized or maximize |  |
| WOY,WeekOfYear | - present Week of Year (1-52) |  |
| Year | - present Year (2007 ) |  |
| YearOdd | - a 1 if the year number is odd else 0 |  |
|  |  | 1 = HostedSite |

The default property for all system objects is value.  Sys.PointsInAlarm is the same as Sys.PointsInAlarm.Value.  Sone objects also support a .Name property, as in Sys.Sitename.Name,  This include

| AlarmState.name | - returns “Alarm State:” |
| --- | --- |
| CommError.name | - returns “Comm. Status:” |
| CommHealth.name | - returns “Comm. Status:” |
| Date.name | - returns “Date:” |
| DateTime.name | - returns “Date / Time:” |
| Dawn.name | - returns “Dawn:” |
| Dusk.name | - returns “Dusk:” |
| Health.name | - returns “Scan Time:” |
| LongDate.name | - returns “Date:” |
| Now.name | - returns “Date / Time:” |
| PointsInAlarm.name | - returns “Points In Alarm:” |
| ProcHealth.name | - returns “Status:” |
| ScanRate.name | - returns “Scan Time:” |
| Scantime.name | - returns “Scan Time:” |
| Season.name | - returns “Season:” |
| ShortDate.name | - returns “Date:” |
| ShortTime.name | - returns “Time:” |
| Sitename.name | - returns “Site:” |
| Status.name | - returns “Status:” |
| Sunrise.name | - returns “Dawn:” |
| Sunset.name | - returns “Dusk:” |
| Time.name | - returns “Time:” |
| Version.name | - returns “Version:” |

All others will return the object name

Available Properties

Class – SUB (Subsystems Data)

Alias			-Alias of the Subsystem Thread

Alarmstate		- Alarmstate of the subsystem

Alarmstep		- As in Points, the alarm step that has processed

LastKnownGood	- Date and Time of the last successful scan of any       points

SubsystemType	- Fixed Values of the known subsystems

CommError		- 1 if Now-LastKnowGood > 15 minutes else 0

Available Properties

Class - PNT	(used generically for all points)

Address		The address within the subsystem

AlarmState		0 = Not Alarmed, 1= Alarmed, 3 = Acknowledged

Alarmstep		how far through the alarm process

AlarmLevel		Level of the alarm

Alias			The alias of this point (probably not needed)

COV			Number of minutes (decimal) since change in value

Details		Numeric value from points.instrument (see txtDetails)

DisabledPosition	where to set the point when it’s off

Groupname		what group (if any) does this point belong to

LastAltered		date time that it was last updated (any change)

LastRead		date time that it was last successfully read

LastCOV		date time of the last change in value

Deviation		difference between Proof Values

LogFrequency	how often does it get logged (minutes)

Name			the name of the point

NameAndtxtValue	returns the name and value of the point

NameAndValue   	same as NameAndtxtValue

NTV			same as NameAndtxtValue

NV			same as NameAndtxtValue

NextCOS		Next time a Change of State is to occur

NextLogDateTime	the next date time the point will be logged

Node			processing node of this poing

NumericID		the numeric ID for this point

OutputAlias		The alias name used in alarm_processes table

Override		1 = overridden, 0 = automatic

OverrideUntilDate	when does it expire

PointType		The point type or ‘class’ (AI, AO, DI…)

Proof			0=Not checked, 1= Proof Good, 2=No Proof

Reason		numeric reason for the point’s state

RecNum		Record Number internal to Proc

Reliability		% of communications reliability (0-1)

RunHours		Cumulative Run hours (DI, DO, Sched, Logic)

SetPoint		depending on point type, the setpoint to achieve

Subsystem		Alias name of the subsystem

SubsystemType	What hardware is being used

txtDetails		Text value from points.instrument (see Details)

txtReason		textual reason for the point’s state

txtValue	textual value of the point (value @ format with eng units)

txtReliability	textual mode (0-100%)

Value			the raw value of the point

OffDuration		If OFF, how long has it been off (minutes) else 0

OffLatch		If OFF, how long has it been off (minutes) else 999

Off15			else 16

OffFor			in conversion + 1

OnDuration		If ON, how long has it been on (minutes) else 0

OnLatch		If ON, how ling has it been on (minutes) else 999

Commstatus		0 – unknown (Gray)

1 – Good Read (Green)

2 – Missed One (Yellow)

3 – No Comm (Red)

PMSState		State of PMS for this point 1=occ, 0=unocc

Available Properties

Class – AI

Deadband		Hysterysus of the value around alarm limits

DisplayFormat	how to display and apply to txtValue

EngUnits		Engineering Units used in txtValue

HighAlarm		Alarm level on the high end

HighThreshold	Maximum value of the point

LowAlarm		Alarm level on the low end

LowThreshold	Minimum value of the point

MaxScale		Span

MinScale		Zero

ScaleAdjust		Calibration adjustment

Smoothing		the number of seconds to “smooth” the readings

Class – AO

DisplayFormat	how to display and apply to txtValue

EngUnits		Engineering Units used in txtValue

MaxScale		Span

MinScale		Zero

MaxSetpoint		What is the maximum value that can be set

MinSetpoint		What is the minimum value that can be set

IncrementSetpoint	What is the incremental change in the setpoint

Class – ASIC1

DeadbandCool	Cooling Hysterysus

DeadbandHeat	Heating Hysterysus

Deadband		Hysterysus of the value around alarm limits

DemandShedLevel	COP to look at for demand level

DisplayFormat	how to display and apply to txtValue

EngUnits		Engineering Units used in txtValue

LightSched		COP to look at for lighting schedule

OccSched		COP to look at for occupied schedule

OvertimeAllowed	in minutes

WarmUpSched	COP to look at for warm-up schedule

OperatingMode	read from the controllers

UnOccHighSetpoint	Unoccupied cooling setpoint

UnOccLowSetpoint	Unoccupied heating setpoint

UserAdjust		how much change can the user make to setpoing (+/-)

Class – DI

ClosedLabel		What’s it say when it is on or true

NormallyClosed    	1 if True 0 if False

OpenLabel		What’s it say when it is open or off

Class – DO

CycleEventTime	The next time the duty cycle will process

ClosedLabel		What’s it say when it is on or true

NormallyClosed    	1 if True 0 if False

OpenLabel		What’s it say when it is open or off

See also OnDuration, OffDuration, OnLimit, OffLimit

Class – Logic

AlarmOption		As defined in AI / DI

AnalogOrDigital	0=Analog, 1 = Digital, 2 = Textual

CalculationTimer	How often to process the calculation (seconds)

Deadband		Deadband is used for alarming only

DisplayFormat	how to display and apply to txtValue

EngUnits		Engineering Units used in txtValue

Equation

HighAlarm

LowAlarm

MaxScale

MinScale

Vxx (1-20)

Class – MVI / MVO

None defined

Class – Meter

ActiveTarget		What target is the meter using now

Consumption		The consumption of the meter in this period

Demand		The demand of the meter in this period

FloatDown		The percentage to float the target down

FloatUp		The percentage to float the target up

InDemandDateTime	When did it go over the target

LastEOD		Date / Time of the last end of demand period

NextEOD

NextTargetTime	Date / Time to reset the target

RateLastMinute	Rate of usage during the last minute

ShedLevel		Present Shedding level of the meter

Class – PID

CalculationTime	Time in seconds between recalculating

D			From database

DirectActing		Output Rise on Error Rise  (0/1)

FeedBack		Result of the PID

I			From database

MaxChange		Maximum Change per evaluation

MaxRange		High Clamp within MinScale / MaxScale

MaxScale		Span

MinRange		Low Clamp within MinScale / Max Scale

MinScale		Zero

P			From database

PIDError		PID Calc – present error (feedback vs setpoint)

PIDIntegralSum	PID Calc – Integral Sum (cumulative error)

StartAt		Starting value

StartHold		How long to stay at StartAt when activate (minutes)

Class – Sched

DelayOn		IF On how many minutes since Last On

Else how many minutes until next On

DelayOff		IF Off how many minutes since Last Off

Else how many minutes until next Off

LastOff		Minutes since last off time

LastOn		Minutes since last on time

NextOff		Minutes until next SCHEDULED off time

NextOn		Minutes until next SCHEDULED on time

Class – Timer

None defined yet