Control IQ – Butler Driver Details

This document contains the details for using the Butler / Enercon Driver

Personality field details in the Subsystem table

RefreshInterval=[0]		= Wait Time (in seconds) between rescans

InterFrameTimer=[100]	= Number of milliseconds between the TX characters

This driver supports 2021,2022,2032x,2051,2033,21xx devices through a 2011/2008

Address 254 and 255 are reserved for broadcast address

Address Schema = Address.Position

Subsystem Setting   COM1:1200,N,7,2

Subsystem Type = "Bulter"

For ICMs (21xx)

Set the point up as a "Butler" subsystem with an ASIC1 point type

Fields used in ASIC1 Details are

Setpoint

Occ Schedule

Display Format

EngUnits

It takes two+ consecutive errors from the devices before the start reporting that there is

a communication problem.

Error  -1  - The device responded but there is an error on the transmission

Error  -2  - There is no response from the device

Error  -3  - The device is on the first scan since restarting proc (this should not appear)

Note ANY override to a 21xx puts it in Total ShutDown.  This is the method to

"reset" the 21xx.  For this reason, DON'T set the "IncludeInSetpoint=1" for a

21xx device.

Address is set by the dip switch on the board

Position is decoded as

DO	0 - Primary Output	[123.0]

DO  	1 - Secondary Output [123.1]

AO  0 - Primary output (on the secondary address)  [124.0]

This requires a 2032A as the master

If no Scaling in the AO screen it assumes 0-100

The AO is only 4 bit (0-15 scales 0-100%) so output is rather crude

The AO is either 1-5 vdc or 4-20ma

AI  0 - Analog Input [123.0]

If no Scaling in the AI screen it assums 0-127 (temperature)

Raw data is 7 bit (0-127) so the temperature is in full degrees

DI  10 - Digital Input #1 (called "Prove Input")

DI  11 - Digital Input #2 (called "Timed Override")

DI  10 - AO Board Terminals 10/11 - Note these are wet inputs

DI  11 - AO Board Terminals 9/10

DI  12 - AO Board Terminals 7/8

Meter  8 (default) use 8 bit counter  (a 0 assumes 8 bit)   [123.0 = 123.8]

Meter 12  use the 12 bit counter   [123.12] (this was a special chip)

ASIC1  0 - Read / Write to the 21xx.  This reports similar to an ASIC1