Control IQ – Functional Devices Driver Details

This document contains the details for using the Functional Driver

Subsystem Type:		FunDev

Personality field details in the Subsystem table

RefreshInterval=[30]	= Wait Time (in seconds) between rescans of AIs and DIs

DefaultSetpoint=[72]    = Set the default UC202 Setpoint for Function 61

Addressing

Addressing Schema

[SynthesizerAddress].TransceiverAddress.Parameter

NOTE if the SynthesizerAddress is ommited, then the driver assumes a single synthesizer on the port.  If the Synthesizer address IS provided, the address MUST be 1 through 31.  Synthesizer Address 0 is NOT supported.  You may have a single synthesizer address (lets     say "1") and that would indicate to the driver, that the synthesizer needs to be shut down when it had completed it’s transmit.  This is used when a Functional Devices, and Scientific Controls transmitter is on the same power distribution system.

Where

SynthesizerAddress  	- the address of the Synthesizer - 1-32

TransceiverAddress  	- 1-1024  (Note the DIP switch address is 1 less 					   than the value DIP=0 is Address=1)

Parameter	- 1     	= Meter (accumulator)

2     	= AI

3     	= AI as Second Address (UC202)

4-9   	= AIs	(Future)

10    	= DI1	DI1 on RTC7/9

11    	= DI2	DI2 on RTC7/9

12    	= DI1   Latched

13    	= DI2   Latched

14	= Command State (2nd Byte or D command)

20	= Bit 1 on highest byte of Return Data from "A" command (AI)

21	= Bit 2 on highest byte of Return Data from "A" command (AI)

22	= Bit 3 on highest byte of Return Data from "A" command (AI)

23	= Bit 4 on highest byte of Return Data from "A" command (AI)

24	= Bit 5 on highest byte of Return Data from "A" command (AI)

25	= Bit 6 on highest byte of Return Data from "A" command (AI)

26	= Bit 7 on highest byte of Return Data from "A" command (AI)

30	= Bit 1 on highest byte of Return Data from "B" command (AI)

31	= Bit 2 on highest byte of Return Data from "B" command (AI)

32	= Bit 3 on highest byte of Return Data from "B" command (AI)

33	= Bit 4 on highest byte of Return Data from "B" command (AI)

34	= Bit 5 on highest byte of Return Data from "B" command (AI)

35	= Bit 6 on highest byte of Return Data from "B" command (AI)

36	= Bit 7 on highest byte of Return Data from "B" command (AI)

40	= Bit 1 on highest byte of Return Data from "D" command (DI)

41	= Bit 2 on highest byte of Return Data from "D" command (DI)

42	= Bit 3 on highest byte of Return Data from "D" command (DI)

43	= Bit 4 on highest byte of Return Data from "D" command (DI)

44	= Bit 5 on highest byte of Return Data from "D" command (DI)

45	= Bit 6 on highest byte of Return Data from "D" command (DI)

46	= Bit 7 on highest byte of Return Data from "D" command (DI)

50    	= DO1

51	= DO2

52-59	= DOs	(Future)

60	= AO	Direct

61    	= AO    Setpoint Adjustment to UC202

62-69	= AOs	(Future)

AIs and AOs are scaled 0-255 based on the values in the Class_AI / Class_AO tables for Zero and Span.  I.E. for a 1000 ohm temperature sensor, Zero= -40(f) and Span= 215(f).  A 1K ohm resistor produces 70 deg F.  In a UC202 the scaling is 40 to 103.

AOs (on a RTC7) appears to be 0-10vdc, however testing (without a load) produced 1-11 vdc output.

DIs actually come back with the bit set (1) if the DI is open and (0) if the DI is closed.  The driver reverses this and returns a 1 when the input is shorted and a 0 when the input is open.  The DI actually brings back the status of the upper most byte of the return data.

Supported Commands

xxM	- Change Sythesizer address (wake it up)  (xx = 1-31)

xxxxF	- Send Off command to xxxx

xxxxN	- Send On command to xxxx

xxxxH	- Send Half command to xxxx

xxxxA	- Read Analog Input / Meter from xxxx

xxxxB   - Read Analog Input from Secondary Address

xxxxD	- Read Digital Input(s) from xxxx

xxxxL	- Read Latched Digital Inputs from xxxx

xxxxR	- Reset Latched Digital Inputs (follows the L command)

xxxxVhh - Send Hex Value (AO) to xxxx