Control IQ – YorkTalk XL Driver Details

This document contains the details for using the YorkTalk XL driver.

Personality field details in the Subsystem table

Access=[5555]	= The password to gain access to the XL panels on the      comm line

Addressing

The addressing schema is Chiller.Parameter

Where:

Chiller -  is the address of the XL board)

Parameter - Number are as follows:

91	Chiller Start / Stop				DO	(On / Off)

92	Leaving Water Set Point			AO	(40 degrees)

93	Current Set Point				A0	(100 percent)

1  - Leaving Chilled Water Setpoint			AI

2  - Load Limit % Setpoint				AI

9  - Leaving Chilled Water Temperature		AI

10 - Entering Chilled Water Temperature		AI

11 - Evaporator Pressure				AI

12 - Condenser Pressure				AI

13 - Oil Pressure					AI

14 - Entering Condenser Water Temp		AI

15 - Leaving Condenser Water Temp		AI

16 - Percent Motor Current				AI

17 - Phase A Amps					AI

18 - Phase B Amps					AI

19 - Phase C Amps					AI

20 - Phase A-B Volts					AI

21 - Phase B-C Volts					AI

22 - Phase A-C Volts					AI

25 - Evap Saturation Temp				AI

26 - Cond Saturation Temp				AI

27 - Discharge Temp					AI

28 - Oil Temp						AI

29 - Purge Pressure					AI

30 - Run Hour						AI

31 - Cumulative Starts				AI

32 - Low Oil Transducer Pressure			AI

33 - High Oil Transducer Pressure			AI

34 - Compressor Motor Status			DI

35 - Vent Sol. Status					DI

36 - CHW Pump Status					DI

37 - Start Switch (1=Stop/Reset,  0=Run/Start)		DI

38 - CHW Pump Flow Status					DI

46 - Adaptive Capacity Control (ACC) Valid Surge Map	DI

47 - ACC New Surge Map					DI

48 - VSD Cooing Pump Running (0=Stopped)		DI

49 - VSD IEEE 519 Filter Present (0=No)			DI

50 - Surge Detection Type (0=Delta P/P, 1=Current)	DI

54 - Anti-Recycle Time Left					AI

55 - Operating Mode (1=Ser, 2=Loc, 3=Rem)		AI

56 - Operation Code (see chart)				Lookup

57 - Safety Code (see chart)					Lookup

58 - Cycling Code(see chart)					Lookup

59 - VSD Internal Temp					AI

60 - VSD Converter Heatsink Temp				AI

61 - ACC PRV position					AI

62 - ACC Frozen O/P Freq					AI

63 - Refrigerant Level Setpoint				AI

64 - Proximity Sensor Actual Position			AI

65 - Proximity Sensor Reference Position			AI

66 - Drain Line Thermocouple Temperature			AI

67 - ACC Frozen Delta P/P					DI

68 - VSD Output Voltage					DI

69 - VSD Input KW						DI

70 - VSD I/p MWH						DI

71 - VSA DC Link Voltage					DI

72 - VSD DC Link Current					DI

73 - VSD Surge Current					DI

74 - VSA Output Frequency					DI

75 - VSD Maximum Voltage THD				DI

76 - VSD Maximum Current THD				DI

77 - VSD Input KVA						DI

Operator Codes  (Address x-56)

0	Normal Operation

1	High Condensor Pressure

2	Low Evaporator Pressure

3	High Current Limit

6	Cond. or Evap Transducer Error

8 	RTC Battery Failure

Safety Code  (Address x-57)

0	No Malfunction

1	Low Evaporator Pressure

2	Low Evaporator Pressure- Brine

3	Low Oil Pressure

4	High Condenser Pressure

5	High Evap Pressure

6	High Discharge Temperature

7	High Oil Temperature

8	Power Fail - Manual Restart

9	High Oil Pressure

10	Starter Malfunction Code

11	Auxiliary

12	Low Discharge Pressure

13	Current Unbalance

31	Faulty Oil Transducer

33	Faulty Condenser Transducer

34	Oil Transducer Error

35	Proximity Sensor Fault

36	High Drain Line Temperature

37	Faulty Proximity Sensor

38	Open Thermocouple

Cycling Code  (Address x-58)

0	No Malfunction

1	Not Used

2	Chilled Water Flow Fault

3	Remote Cycling

4	Multi-unit cycling

5	Low Water Temperature

6	Internal Time Clock

7	Power Failure - Autostart

8	Vane Mtr Switch Open

9	Anti-Recycle

10	Motor Controller

11	Power Fault

12	SSS AC Under Voltage

13	AC Under Voltage

15	AC Over Voltage

32	Low Oil Temp-Diff

39	DC Under Voltage